# Dispatch Simulation with Charging & Dispatch Rules

48-Hour Simulation | Load: 25 MW | DG: 27 MW | BESS: 100 MWh / 10 MW | Efficiency: 85%

# Template 0: Solar + BESS Only (No DG)

Merit Order: Solar → BESS → Unserved

## Dispatch Rules

1. Solar serves load first (direct priority)

2. BESS discharges to cover any remaining load after solar

3. If BESS depleted (SoC ≤ 10%), load goes unserved

4. No DG available in this topology

## Charging Rules

1. BESS charges ONLY from excess solar (after load is served)

2. Charge rate limited by: BESS power (10 MW), available room to max SoC

3. Charge efficiency applied: Energy stored = Power × √0.85

4. If BESS full (SoC = 90%), excess solar is curtailed

## Key Constraints

• BESS cannot charge and discharge in the same hour

• SoC bounded: 10% (min) to 90% (max)

• No DG backup - unserved energy if BESS depleted

## Hourly Simulation Data

| Hr | Solar | DG | BESS Pwr | BESS E | SoC% | State | ChgFrom | Load | Supply | Deficit | Sol→Ld | BESS→Ld | DG→Ld |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 |
| 1 | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 |
| 2 | 0 | 0 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 |
| 3 | 0 | 0 | 6.88 | 10 | 10 | Discharging | - | 25 | 6.88 | 18.12 | 0 | 6.88 | 0 |
| 4 | 0.57 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.57 | 24.43 | 0.57 | 0 | 0 |
| 5 | 2.02 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.02 | 22.98 | 2.02 | 0 | 0 |
| 6 | 8.71 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.71 | 16.29 | 8.71 | 0 | 0 |
| 7 | 10.81 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.81 | 14.19 | 10.81 | 0 | 0 |
| 8 | 18.77 | 0 | 0 | 10 | 10 | Idle | - | 25 | 18.77 | 6.23 | 18.77 | 0 | 0 |
| 9 | 17.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 17.92 | 7.08 | 17.92 | 0 | 0 |
| 10 | 21.07 | 0 | 0 | 10 | 10 | Idle | - | 25 | 21.07 | 3.93 | 21.07 | 0 | 0 |
| 11 | 22.94 | 0 | 0 | 10 | 10 | Idle | - | 25 | 22.94 | 2.06 | 22.94 | 0 | 0 |
| 12 | 49.85 | 0 | 10 | 19.22 | 19.22 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 13 | 50.83 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 14 | 17.66 | 0 | 7.34 | 20.48 | 20.48 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0 |
| 15 | 5.61 | 0 | 9.66 | 10 | 10 | Discharging | - | 25 | 15.27 | 9.73 | 5.61 | 9.66 | 0 |
| 16 | 8.52 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.52 | 16.48 | 8.52 | 0 | 0 |
| 17 | 5.42 | 0 | 0 | 10 | 10 | Idle | - | 25 | 5.42 | 19.58 | 5.42 | 0 | 0 |
| 18 | 2.43 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.43 | 22.57 | 2.43 | 0 | 0 |
| 19 | 0.73 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.73 | 24.27 | 0.73 | 0 | 0 |
| 20 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 21 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 22 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 23 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 0 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 1 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 3 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 4 | 1.25 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.25 | 23.75 | 1.25 | 0 | 0 |
| 5 | 3.35 | 0 | 0 | 10 | 10 | Idle | - | 25 | 3.35 | 21.65 | 3.35 | 0 | 0 |
| 6 | 6.28 | 0 | 0 | 10 | 10 | Idle | - | 25 | 6.28 | 18.72 | 6.28 | 0 | 0 |
| 7 | 12.72 | 0 | 0 | 10 | 10 | Idle | - | 25 | 12.72 | 12.28 | 12.72 | 0 | 0 |
| 8 | 26.88 | 0 | 1.88 | 11.73 | 11.73 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 9 | 34.82 | 0 | 9.82 | 20.79 | 20.79 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 10 | 30.45 | 0 | 5.45 | 25.81 | 25.81 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 11 | 27.44 | 0 | 2.44 | 28.06 | 28.06 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 12 | 29.18 | 0 | 4.18 | 31.91 | 31.91 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 13 | 12.43 | 0 | 10 | 21.07 | 21.07 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0 |
| 14 | 15.36 | 0 | 9.64 | 10.61 | 10.61 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0 |
| 15 | 19.44 | 0 | 0.56 | 10 | 10 | Discharging | - | 25 | 20 | 5 | 19.44 | 0.56 | 0 |
| 16 | 11.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 11.92 | 13.08 | 11.92 | 0 | 0 |
| 17 | 10.96 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.96 | 14.04 | 10.96 | 0 | 0 |
| 18 | 4.89 | 0 | 0 | 10 | 10 | Idle | - | 25 | 4.89 | 20.11 | 4.89 | 0 | 0 |
| 19 | 1.18 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.18 | 23.82 | 1.18 | 0 | 0 |
| 20 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 21 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 22 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |
| 23 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 |

# Template 1: Green Priority

Merit Order: Solar → BESS → DG → Unserved

## Dispatch Rules

1. Solar serves load first (highest priority)

2. BESS discharges to cover remaining load

3. DG activates ONLY when Solar + BESS cannot meet load (last resort)

4. DG runs at Full Capacity (27 MW) when ON

5. DG does NOT turn on proactively to charge BESS

## Charging Rules

1. BESS charges from excess solar (priority 1)

2. BESS charges from excess DG when DG is running and load is served

3. Charging only happens when BESS is not discharging

4. Charge rate limited by BESS power (10 MW)

## Key Constraints

• BESS cannot charge and discharge in the same hour

• DG is reactive only - does not proactively charge BESS

• Green-first philosophy: maximize solar/BESS usage

## Hourly Simulation Data

| Hr | Solar | DG | BESS Pwr | BESS E | SoC% | State | ChgFrom | Load | Supply | Deficit | Sol→Ld | BESS→Ld | DG→Ld |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 27 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 25 | 0 | 0 | 10 | 15 |
| 1 | 0 | 27 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 25 | 0 | 0 | 10 | 15 |
| 2 | 0 | 27 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 25 | 0 | 0 | 10 | 15 |
| 3 | 0 | 27 | 6.88 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 6.88 | 18.12 |
| 4 | 0.57 | 27 | 2.57 | 12.37 | 12.37 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43 |
| 5 | 2.02 | 27 | 2.18 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 2.02 | 2.18 | 20.8 |
| 6 | 8.71 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 8.71 | 0 | 16.29 |
| 7 | 10.81 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 10.81 | 8.5 | 5.69 |
| 8 | 18.77 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 18.77 | 0 | 6.23 |
| 9 | 17.92 | 0 | 7.08 | 11.54 | 11.54 | Discharging | - | 25 | 25 | 0 | 17.92 | 7.08 | 0 |
| 10 | 21.07 | 27 | 1.42 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 21.07 | 1.42 | 2.51 |
| 11 | 22.94 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 22.94 | 0 | 2.06 |
| 12 | 49.85 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 13 | 50.83 | 0 | 10 | 37.66 | 37.66 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 14 | 17.66 | 0 | 7.34 | 29.7 | 29.7 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0 |
| 15 | 5.61 | 27 | 10 | 18.85 | 18.85 | Discharging | - | 25 | 25 | 0 | 5.61 | 10 | 9.39 |
| 16 | 8.52 | 27 | 8.16 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 8.52 | 8.16 | 8.32 |
| 17 | 5.42 | 27 | 7.42 | 16.84 | 16.84 | Charging | DG | 25 | 25 | 0 | 5.42 | 0 | 19.58 |
| 18 | 2.43 | 27 | 6.31 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 2.43 | 6.31 | 16.26 |
| 19 | 0.73 | 27 | 2.73 | 12.52 | 12.52 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27 |
| 20 | 0 | 27 | 2.32 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 2.32 | 22.68 |
| 21 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 |
| 22 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3 |
| 23 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 |
| 0 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3 |
| 1 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 |
| 2 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3 |
| 3 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 |
| 4 | 1.25 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 1.25 | 1.7 | 22.05 |
| 5 | 3.35 | 27 | 5.35 | 14.93 | 14.93 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65 |
| 6 | 6.28 | 27 | 4.55 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 6.28 | 4.55 | 14.17 |
| 7 | 12.72 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 12.72 | 0 | 12.28 |
| 8 | 26.88 | 0 | 1.88 | 20.95 | 20.95 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 9 | 34.82 | 0 | 9.82 | 30.01 | 30.01 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 10 | 30.45 | 0 | 5.45 | 35.03 | 35.03 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 11 | 27.44 | 0 | 2.44 | 37.28 | 37.28 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 12 | 29.18 | 0 | 4.18 | 41.13 | 41.13 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 |
| 13 | 12.43 | 27 | 10 | 30.29 | 30.29 | Discharging | - | 25 | 25 | 0 | 12.43 | 10 | 2.57 |
| 14 | 15.36 | 0 | 9.64 | 19.83 | 19.83 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0 |
| 15 | 19.44 | 0 | 5.56 | 13.8 | 13.8 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0 |
| 16 | 11.92 | 27 | 3.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 11.92 | 3.5 | 9.58 |
| 17 | 10.96 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 10.96 | 0 | 14.04 |
| 18 | 4.89 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 4.89 | 8.5 | 11.61 |
| 19 | 1.18 | 27 | 3.18 | 12.93 | 12.93 | Charging | DG | 25 | 25 | 0 | 1.18 | 0 | 23.82 |
| 20 | 0 | 27 | 2.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 2.7 | 22.3 |
| 21 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 |
| 22 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3 |
| 23 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 |

# Template 2: DG Night Charge

Night: DG Proactive | Day: Green Only

## Dispatch Rules

1. NIGHT (18:00-06:00): DG turns ON proactively when night starts

2. NIGHT: DG serves load, excess charges BESS

3. NIGHT: DG turns OFF when SoC reaches 80% threshold

4. NIGHT: If DG OFF, BESS discharges to serve load

5. DAY (06:00-18:00): DG is DISABLED (not allowed to run)

6. DAY: Solar serves load first, BESS covers remainder

7. DAY: If BESS depleted, load goes unserved (or Emergency DG if enabled)

## Charging Rules

1. NIGHT: BESS charges from excess DG (when DG ON and load served)

2. DAY: BESS charges from excess solar only

3. Charging stops when SoC reaches 90%

## Key Constraints

• DG proactive at night (not SoC-triggered like T4/5/6)

• Day is strictly green unless emergency override enabled

• BESS sized to cover daytime load with solar support

## Hourly Simulation Data

| Hr | Solar | DG | BESS Pwr | BESS E | SoC% | State | ChgFrom | Load | Supply | Deficit | Sol→Ld | BESS→Ld | DG→Ld | Period |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night |
| 1 | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night |
| 2 | 0 | 27 | 2 | 30.15 | 30.15 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 3 | 0 | 27 | 2 | 31.99 | 31.99 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 4 | 0.57 | 27 | 2.57 | 34.36 | 34.36 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43 | Night |
| 5 | 2.02 | 27 | 4.02 | 38.07 | 38.07 | Charging | DG | 25 | 25 | 0 | 2.02 | 0 | 22.98 | Night |
| 6 | 8.71 | 0 | 10 | 27.22 | 27.22 | Discharging | - | 25 | 18.71 | 6.29 | 8.71 | 10 | 0 | Day |
| 7 | 10.81 | 0 | 10 | 16.38 | 16.38 | Discharging | - | 25 | 20.81 | 4.19 | 10.81 | 10 | 0 | Day |
| 8 | 18.77 | 0 | 5.88 | 10 | 10 | Discharging | - | 25 | 24.65 | 0.35 | 18.77 | 5.88 | 0 | Day |
| 9 | 17.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 17.92 | 7.08 | 17.92 | 0 | 0 | Day |
| 10 | 21.07 | 0 | 0 | 10 | 10 | Idle | - | 25 | 21.07 | 3.93 | 21.07 | 0 | 0 | Day |
| 11 | 22.94 | 0 | 0 | 10 | 10 | Idle | - | 25 | 22.94 | 2.06 | 22.94 | 0 | 0 | Day |
| 12 | 49.85 | 0 | 10 | 19.22 | 19.22 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day |
| 13 | 50.83 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day |
| 14 | 17.66 | 0 | 7.34 | 20.48 | 20.48 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0 | Day |
| 15 | 5.61 | 0 | 9.66 | 10 | 10 | Discharging | - | 25 | 15.27 | 9.73 | 5.61 | 9.66 | 0 | Day |
| 16 | 8.52 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.52 | 16.48 | 8.52 | 0 | 0 | Day |
| 17 | 5.42 | 0 | 0 | 10 | 10 | Idle | - | 25 | 5.42 | 19.58 | 5.42 | 0 | 0 | Day |
| 18 | 2.43 | 27 | 4.43 | 14.08 | 14.08 | Charging | DG | 25 | 25 | 0 | 2.43 | 0 | 22.57 | Night |
| 19 | 0.73 | 27 | 2.73 | 16.6 | 16.6 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27 | Night |
| 20 | 0 | 27 | 2 | 18.45 | 18.45 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 21 | 0 | 27 | 2 | 20.29 | 20.29 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 22 | 0 | 27 | 2 | 22.13 | 22.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 23 | 0 | 27 | 2 | 23.98 | 23.98 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 0 | 0 | 27 | 2 | 25.82 | 25.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 1 | 0 | 27 | 2 | 27.66 | 27.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 2 | 0 | 27 | 2 | 29.51 | 29.51 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 3 | 0 | 27 | 2 | 31.35 | 31.35 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 4 | 1.25 | 27 | 3.25 | 34.35 | 34.35 | Charging | DG | 25 | 25 | 0 | 1.25 | 0 | 23.75 | Night |
| 5 | 3.35 | 27 | 5.35 | 39.28 | 39.28 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65 | Night |
| 6 | 6.28 | 0 | 10 | 28.43 | 28.43 | Discharging | - | 25 | 16.28 | 8.72 | 6.28 | 10 | 0 | Day |
| 7 | 12.72 | 0 | 10 | 17.59 | 17.59 | Discharging | - | 25 | 22.72 | 2.28 | 12.72 | 10 | 0 | Day |
| 8 | 26.88 | 0 | 1.88 | 19.32 | 19.32 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day |
| 9 | 34.82 | 0 | 9.82 | 28.38 | 28.38 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day |
| 10 | 30.45 | 0 | 5.45 | 33.4 | 33.4 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day |
| 11 | 27.44 | 0 | 2.44 | 35.65 | 35.65 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day |
| 12 | 29.18 | 0 | 4.18 | 39.5 | 39.5 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day |
| 13 | 12.43 | 0 | 10 | 28.66 | 28.66 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0 | Day |
| 14 | 15.36 | 0 | 9.64 | 18.2 | 18.2 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0 | Day |
| 15 | 19.44 | 0 | 5.56 | 12.17 | 12.17 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0 | Day |
| 16 | 11.92 | 0 | 2 | 10 | 10 | Discharging | - | 25 | 13.92 | 11.08 | 11.92 | 2 | 0 | Day |
| 17 | 10.96 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.96 | 14.04 | 10.96 | 0 | 0 | Day |
| 18 | 4.89 | 27 | 6.89 | 16.35 | 16.35 | Charging | DG | 25 | 25 | 0 | 4.89 | 0 | 20.11 | Night |
| 19 | 1.18 | 27 | 3.18 | 19.28 | 19.28 | Charging | DG | 25 | 25 | 0 | 1.18 | 0 | 23.82 | Night |
| 20 | 0 | 27 | 2 | 21.13 | 21.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 21 | 0 | 27 | 2 | 22.97 | 22.97 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 22 | 0 | 27 | 2 | 24.82 | 24.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |
| 23 | 0 | 27 | 2 | 26.66 | 26.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night |

# Template 3: DG Blackout Window

Blackout (22:00-06:00): DG Disabled | Outside: Normal

## Dispatch Rules

1. BLACKOUT (22:00-06:00): DG is strictly DISABLED

2. BLACKOUT: Solar → BESS → Unserved (no DG allowed)

3. OUTSIDE BLACKOUT: Solar → BESS → DG → Unserved

4. DG is reactive (activates only when Solar + BESS insufficient)

5. DG runs at Full Capacity (27 MW) when ON

## Charging Rules

1. BESS charges from excess solar (always available)

2. BESS charges from excess DG (outside blackout only)

3. No charging during blackout from DG

## Key Constraints

• DG cannot run during blackout window (noise/emissions restriction)

• No emergency override during blackout

• BESS must be sized to survive blackout hours

## Hourly Simulation Data

| Hr | Solar | DG | BESS Pwr | BESS E | SoC% | State | ChgFrom | Load | Supply | Deficit | Sol→Ld | BESS→Ld | DG→Ld | Period |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Blackout |
| 1 | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Blackout |
| 2 | 0 | 0 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Blackout |
| 3 | 0 | 0 | 6.88 | 10 | 10 | Discharging | - | 25 | 6.88 | 18.12 | 0 | 6.88 | 0 | Blackout |
| 4 | 0.57 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.57 | 24.43 | 0.57 | 0 | 0 | Blackout |
| 5 | 2.02 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.02 | 22.98 | 2.02 | 0 | 0 | Blackout |
| 6 | 8.71 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 8.71 | 0 | 16.29 | Normal |
| 7 | 10.81 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 10.81 | 8.5 | 5.69 | Normal |
| 8 | 18.77 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 18.77 | 0 | 6.23 | Normal |
| 9 | 17.92 | 0 | 7.08 | 11.54 | 11.54 | Discharging | - | 25 | 25 | 0 | 17.92 | 7.08 | 0 | Normal |
| 10 | 21.07 | 27 | 1.42 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 21.07 | 1.42 | 2.51 | Normal |
| 11 | 22.94 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 22.94 | 0 | 2.06 | Normal |
| 12 | 49.85 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Normal |
| 13 | 50.83 | 0 | 10 | 37.66 | 37.66 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Normal |
| 14 | 17.66 | 0 | 7.34 | 29.7 | 29.7 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0 | Normal |
| 15 | 5.61 | 27 | 10 | 18.85 | 18.85 | Discharging | - | 25 | 25 | 0 | 5.61 | 10 | 9.39 | Normal |
| 16 | 8.52 | 27 | 8.16 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 8.52 | 8.16 | 8.32 | Normal |
| 17 | 5.42 | 27 | 7.42 | 16.84 | 16.84 | Charging | DG | 25 | 25 | 0 | 5.42 | 0 | 19.58 | Normal |
| 18 | 2.43 | 27 | 6.31 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 2.43 | 6.31 | 16.26 | Normal |
| 19 | 0.73 | 27 | 2.73 | 12.52 | 12.52 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27 | Normal |
| 20 | 0 | 27 | 2.32 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 2.32 | 22.68 | Normal |
| 21 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Normal |
| 22 | 0 | 0 | 1.7 | 10 | 10 | Discharging | - | 25 | 1.7 | 23.3 | 0 | 1.7 | 0 | Blackout |
| 23 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Blackout |
| 0 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Blackout |
| 1 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Blackout |
| 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Blackout |
| 3 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Blackout |
| 4 | 1.25 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.25 | 23.75 | 1.25 | 0 | 0 | Blackout |
| 5 | 3.35 | 0 | 0 | 10 | 10 | Idle | - | 25 | 3.35 | 21.65 | 3.35 | 0 | 0 | Blackout |
| 6 | 6.28 | 27 | 8.28 | 17.63 | 17.63 | Charging | DG | 25 | 25 | 0 | 6.28 | 0 | 18.72 | Normal |
| 7 | 12.72 | 27 | 7.04 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 12.72 | 7.04 | 5.24 | Normal |
| 8 | 26.88 | 0 | 1.88 | 11.73 | 11.73 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Normal |
| 9 | 34.82 | 0 | 9.82 | 20.79 | 20.79 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Normal |
| 10 | 30.45 | 0 | 5.45 | 25.81 | 25.81 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Normal |
| 11 | 27.44 | 0 | 2.44 | 28.06 | 28.06 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Normal |
| 12 | 29.18 | 0 | 4.18 | 31.91 | 31.91 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Normal |
| 13 | 12.43 | 27 | 10 | 21.07 | 21.07 | Discharging | - | 25 | 25 | 0 | 12.43 | 10 | 2.57 | Normal |
| 14 | 15.36 | 0 | 9.64 | 10.61 | 10.61 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0 | Normal |
| 15 | 19.44 | 27 | 0.56 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 19.44 | 0.56 | 5 | Normal |
| 16 | 11.92 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 11.92 | 0 | 13.08 | Normal |
| 17 | 10.96 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 10.96 | 8.5 | 5.54 | Normal |
| 18 | 4.89 | 27 | 6.89 | 16.35 | 16.35 | Charging | DG | 25 | 25 | 0 | 4.89 | 0 | 20.11 | Normal |
| 19 | 1.18 | 27 | 5.86 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 1.18 | 5.86 | 17.96 | Normal |
| 20 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Normal |
| 21 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3 | Normal |
| 22 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Blackout |
| 23 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Blackout |

# Template 4: DG Emergency Only

SoC-Triggered: ON ≤ 30%, OFF ≥ 80% | No Time Restrictions

## Dispatch Rules

1. Normal: Solar → BESS → Unserved (DG stays OFF)

2. DG turns ON when SoC drops to/below 30%

3. DG turns OFF when SoC rises to/above 80%

4. ASSIST MODE: When DG ON but DG < Load, BESS assists (covers deficit)

5. RECOVERY MODE: When DG ON and DG ≥ Load, BESS rests and charges

6. DG runs at Full Capacity (27 MW) when triggered

7. No time restrictions - DG can run anytime

## Charging Rules

1. BESS charges from excess solar (when DG OFF)

2. BESS charges from excess DG in Recovery Mode

3. No charging in Assist Mode (BESS is discharging)

## Key Constraints

• Deadband hysteresis: ON ≤ 30%, OFF ≥ 80%

• DG is SoC-triggered, not load-triggered

• Cycle limit enforcement disabled (monitor-only)

## Hourly Simulation Data

| Hr | Solar | DG | BESS Pwr | BESS E | SoC% | State | ChgFrom | Load | Supply | Deficit | Sol→Ld | BESS→Ld | DG→Ld | DG Mode |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | OFF |
| 1 | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | OFF |
| 2 | 0 | 27 | 2 | 30.15 | 30.15 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 3 | 0 | 27 | 2 | 31.99 | 31.99 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 4 | 0.57 | 27 | 2.57 | 34.36 | 34.36 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43 | ON-Recovery |
| 5 | 2.02 | 27 | 4.02 | 38.07 | 38.07 | Charging | DG | 25 | 25 | 0 | 2.02 | 0 | 22.98 | ON-Recovery |
| 6 | 8.71 | 27 | 10 | 47.29 | 47.29 | Charging | DG | 25 | 25 | 0 | 8.71 | 0 | 16.29 | ON-Recovery |
| 7 | 10.81 | 27 | 10 | 56.51 | 56.51 | Charging | DG | 25 | 25 | 0 | 10.81 | 0 | 14.19 | ON-Recovery |
| 8 | 18.77 | 27 | 10 | 65.73 | 65.73 | Charging | DG | 25 | 25 | 0 | 18.77 | 0 | 6.23 | ON-Recovery |
| 9 | 17.92 | 27 | 10 | 74.95 | 74.95 | Charging | DG | 25 | 25 | 0 | 17.92 | 0 | 7.08 | ON-Recovery |
| 10 | 21.07 | 27 | 10 | 84.17 | 84.17 | Charging | DG | 25 | 25 | 0 | 21.07 | 0 | 3.93 | ON-Recovery |
| 11 | 22.94 | 0 | 2.06 | 81.93 | 81.93 | Discharging | - | 25 | 25 | 0 | 22.94 | 2.06 | 0 | OFF |
| 12 | 49.85 | 0 | 8.75 | 90 | 90 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | OFF |
| 13 | 50.83 | 0 | 0 | 90 | 90 | Idle | - | 25 | 25 | 0 | 25 | 0 | 0 | OFF |
| 14 | 17.66 | 0 | 7.34 | 82.04 | 82.04 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0 | OFF |
| 15 | 5.61 | 0 | 10 | 71.19 | 71.19 | Discharging | - | 25 | 15.61 | 9.39 | 5.61 | 10 | 0 | OFF |
| 16 | 8.52 | 0 | 10 | 60.35 | 60.35 | Discharging | - | 25 | 18.52 | 6.48 | 8.52 | 10 | 0 | OFF |
| 17 | 5.42 | 0 | 10 | 49.5 | 49.5 | Discharging | - | 25 | 15.42 | 9.58 | 5.42 | 10 | 0 | OFF |
| 18 | 2.43 | 0 | 10 | 38.65 | 38.65 | Discharging | - | 25 | 12.43 | 12.57 | 2.43 | 10 | 0 | OFF |
| 19 | 0.73 | 0 | 10 | 27.81 | 27.81 | Discharging | - | 25 | 10.73 | 14.27 | 0.73 | 10 | 0 | OFF |
| 20 | 0 | 27 | 2 | 29.65 | 29.65 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 21 | 0 | 27 | 2 | 31.49 | 31.49 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 22 | 0 | 27 | 2 | 33.34 | 33.34 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 23 | 0 | 27 | 2 | 35.18 | 35.18 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 0 | 0 | 27 | 2 | 37.03 | 37.03 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 1 | 0 | 27 | 2 | 38.87 | 38.87 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 2 | 0 | 27 | 2 | 40.71 | 40.71 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 3 | 0 | 27 | 2 | 42.56 | 42.56 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 4 | 1.25 | 27 | 3.25 | 45.55 | 45.55 | Charging | DG | 25 | 25 | 0 | 1.25 | 0 | 23.75 | ON-Recovery |
| 5 | 3.35 | 27 | 5.35 | 50.49 | 50.49 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65 | ON-Recovery |
| 6 | 6.28 | 27 | 8.28 | 58.12 | 58.12 | Charging | DG | 25 | 25 | 0 | 6.28 | 0 | 18.72 | ON-Recovery |
| 7 | 12.72 | 27 | 10 | 67.34 | 67.34 | Charging | DG | 25 | 25 | 0 | 12.72 | 0 | 12.28 | ON-Recovery |
| 8 | 26.88 | 27 | 10 | 76.56 | 76.56 | Charging | DG | 25 | 25 | 0 | 25 | 0 | 0 | ON-Recovery |
| 9 | 34.82 | 27 | 10 | 85.78 | 85.78 | Charging | DG | 25 | 25 | 0 | 25 | 0 | 0 | ON-Recovery |
| 10 | 30.45 | 0 | 4.58 | 90 | 90 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | OFF |
| 11 | 27.44 | 0 | 0 | 90 | 90 | Idle | - | 25 | 25 | 0 | 25 | 0 | 0 | OFF |
| 12 | 29.18 | 0 | 0 | 90 | 90 | Idle | - | 25 | 25 | 0 | 25 | 0 | 0 | OFF |
| 13 | 12.43 | 0 | 10 | 79.15 | 79.15 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0 | OFF |
| 14 | 15.36 | 0 | 9.64 | 68.7 | 68.7 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0 | OFF |
| 15 | 19.44 | 0 | 5.56 | 62.67 | 62.67 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0 | OFF |
| 16 | 11.92 | 0 | 10 | 51.82 | 51.82 | Discharging | - | 25 | 21.92 | 3.08 | 11.92 | 10 | 0 | OFF |
| 17 | 10.96 | 0 | 10 | 40.97 | 40.97 | Discharging | - | 25 | 20.96 | 4.04 | 10.96 | 10 | 0 | OFF |
| 18 | 4.89 | 0 | 10 | 30.13 | 30.13 | Discharging | - | 25 | 14.89 | 10.11 | 4.89 | 10 | 0 | OFF |
| 19 | 1.18 | 0 | 10 | 19.28 | 19.28 | Discharging | - | 25 | 11.18 | 13.82 | 1.18 | 10 | 0 | OFF |
| 20 | 0 | 27 | 2 | 21.12 | 21.12 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 21 | 0 | 27 | 2 | 22.97 | 22.97 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 22 | 0 | 27 | 2 | 24.81 | 24.81 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |
| 23 | 0 | 27 | 2 | 26.66 | 26.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | ON-Recovery |

# Template 5: DG Day Charge

Day: SoC-Triggered DG | Night: Silent (DG Disabled)

## Dispatch Rules

1. DAY (06:00-18:00): DG allowed (SoC-triggered)

2. DAY: DG turns ON when SoC ≤ 30%, OFF when SoC ≥ 80%

3. DAY: ASSIST MODE when DG < remaining load (BESS helps)

4. DAY: RECOVERY MODE when DG ≥ remaining load (BESS charges)

5. NIGHT (18:00-06:00): DG is DISABLED (silent operation)

6. NIGHT: Solar → BESS → Emergency DG (if enabled) → Unserved

7. SUNSET CUT: DG forced OFF immediately when night starts

## Charging Rules

1. DAY: BESS charges from solar + DG excess in Recovery Mode

2. NIGHT: BESS charges from excess solar only

3. No DG charging at night (DG disabled)

## Key Constraints

• Silent nights for residential areas

• DG SoC-triggered during day only

• Cycle limit monitor-only (no enforcement)

## Hourly Simulation Data

| Hr | Solar | DG | BESS Pwr | BESS E | SoC% | State | ChgFrom | Load | Supply | Deficit | Sol→Ld | BESS→Ld | DG→Ld | Period | DG Mode |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night | OFF |
| 1 | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night | OFF |
| 2 | 0 | 0 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night | OFF |
| 3 | 0 | 0 | 6.88 | 10 | 10 | Discharging | - | 25 | 6.88 | 18.12 | 0 | 6.88 | 0 | Night | OFF |
| 4 | 0.57 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.57 | 24.43 | 0.57 | 0 | 0 | Night | OFF |
| 5 | 2.02 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.02 | 22.98 | 2.02 | 0 | 0 | Night | OFF |
| 6 | 8.71 | 27 | 10 | 19.22 | 19.22 | Charging | Solar+DG | 25 | 25 | 0 | 8.71 | 0 | 16.29 | Day | NORMAL |
| 7 | 10.81 | 27 | 10 | 28.44 | 28.44 | Charging | Solar+DG | 25 | 25 | 0 | 10.81 | 0 | 14.19 | Day | NORMAL |
| 8 | 18.77 | 27 | 10 | 37.66 | 37.66 | Charging | Solar+DG | 25 | 25 | 0 | 18.77 | 0 | 6.23 | Day | NORMAL |
| 9 | 17.92 | 27 | 10 | 46.88 | 46.88 | Charging | Solar+DG | 25 | 25 | 0 | 17.92 | 0 | 7.08 | Day | NORMAL |
| 10 | 21.07 | 27 | 10 | 56.1 | 56.1 | Charging | Solar+DG | 25 | 25 | 0 | 21.07 | 0 | 3.93 | Day | NORMAL |
| 11 | 22.94 | 27 | 10 | 65.32 | 65.32 | Charging | Solar+DG | 25 | 25 | 0 | 22.94 | 0 | 2.06 | Day | NORMAL |
| 12 | 49.85 | 27 | 10 | 74.54 | 74.54 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | NORMAL |
| 13 | 50.83 | 27 | 10 | 83.76 | 83.76 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | NORMAL |
| 14 | 17.66 | 0 | 7.34 | 75.8 | 75.8 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0 | Day | OFF |
| 15 | 5.61 | 0 | 10 | 64.95 | 64.95 | Discharging | - | 25 | 15.61 | 9.39 | 5.61 | 10 | 0 | Day | OFF |
| 16 | 8.52 | 0 | 10 | 54.1 | 54.1 | Discharging | - | 25 | 18.52 | 6.48 | 8.52 | 10 | 0 | Day | OFF |
| 17 | 5.42 | 0 | 10 | 43.26 | 43.26 | Discharging | - | 25 | 15.42 | 9.58 | 5.42 | 10 | 0 | Day | OFF |
| 18 | 2.43 | 0 | 10 | 32.41 | 32.41 | Discharging | - | 25 | 12.43 | 12.57 | 2.43 | 10 | 0 | Night | OFF |
| 19 | 0.73 | 0 | 10 | 21.56 | 21.56 | Discharging | - | 25 | 10.73 | 14.27 | 0.73 | 10 | 0 | Night | OFF |
| 20 | 0 | 0 | 10 | 10.72 | 10.72 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night | OFF |
| 21 | 0 | 0 | 0.66 | 10 | 10 | Discharging | - | 25 | 0.66 | 24.34 | 0 | 0.66 | 0 | Night | OFF |
| 22 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |
| 23 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |
| 0 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |
| 1 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |
| 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |
| 3 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |
| 4 | 1.25 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.25 | 23.75 | 1.25 | 0 | 0 | Night | OFF |
| 5 | 3.35 | 0 | 0 | 10 | 10 | Idle | - | 25 | 3.35 | 21.65 | 3.35 | 0 | 0 | Night | OFF |
| 6 | 6.28 | 27 | 8.28 | 17.63 | 17.63 | Charging | Solar+DG | 25 | 25 | 0 | 6.28 | 0 | 18.72 | Day | NORMAL |
| 7 | 12.72 | 27 | 10 | 26.85 | 26.85 | Charging | Solar+DG | 25 | 25 | 0 | 12.72 | 0 | 12.28 | Day | NORMAL |
| 8 | 26.88 | 27 | 10 | 36.07 | 36.07 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0 | Day | NORMAL |
| 9 | 34.82 | 27 | 10 | 45.29 | 45.29 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0 | Day | NORMAL |
| 10 | 30.45 | 27 | 10 | 54.51 | 54.51 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0 | Day | NORMAL |
| 11 | 27.44 | 27 | 10 | 63.73 | 63.73 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0 | Day | NORMAL |
| 12 | 29.18 | 27 | 10 | 72.95 | 72.95 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0 | Day | NORMAL |
| 13 | 12.43 | 27 | 10 | 82.17 | 82.17 | Charging | Solar+DG | 25 | 25 | 0 | 12.43 | 0 | 12.57 | Day | NORMAL |
| 14 | 15.36 | 0 | 9.64 | 71.71 | 71.71 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0 | Day | OFF |
| 15 | 19.44 | 0 | 5.56 | 65.68 | 65.68 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0 | Day | OFF |
| 16 | 11.92 | 0 | 10 | 54.84 | 54.84 | Discharging | - | 25 | 21.92 | 3.08 | 11.92 | 10 | 0 | Day | OFF |
| 17 | 10.96 | 0 | 10 | 43.99 | 43.99 | Discharging | - | 25 | 20.96 | 4.04 | 10.96 | 10 | 0 | Day | OFF |
| 18 | 4.89 | 0 | 10 | 33.14 | 33.14 | Discharging | - | 25 | 14.89 | 10.11 | 4.89 | 10 | 0 | Night | OFF |
| 19 | 1.18 | 0 | 10 | 22.3 | 22.3 | Discharging | - | 25 | 11.18 | 13.82 | 1.18 | 10 | 0 | Night | OFF |
| 20 | 0 | 0 | 10 | 11.45 | 11.45 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night | OFF |
| 21 | 0 | 0 | 1.34 | 10 | 10 | Discharging | - | 25 | 1.34 | 23.66 | 0 | 1.34 | 0 | Night | OFF |
| 22 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |
| 23 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0 | Night | OFF |

# Template 6: DG Night SoC Trigger

Night: SoC-Triggered DG | Day: Green (DG Disabled)

## Dispatch Rules

1. NIGHT (18:00-06:00): DG allowed (SoC-triggered)

2. NIGHT: DG turns ON when SoC ≤ 30%, OFF when SoC ≥ 80%

3. NIGHT: ASSIST MODE when DG < remaining load (BESS helps)

4. NIGHT: RECOVERY MODE when DG ≥ remaining load (BESS charges)

5. DAY (06:00-18:00): DG is DISABLED (green operation)

6. DAY: Solar → BESS → Emergency DG (if enabled) → Unserved

7. SUNRISE CUT: DG forced OFF immediately when day starts

## Charging Rules

1. NIGHT: BESS charges from DG excess in Recovery Mode

2. DAY: BESS charges from excess solar only

3. No DG charging during day (DG disabled)

## Key Constraints

• Green days maximize solar utilization

• DG runs only at night for recharge

• Cycle limit enforcement allowed (predictable green day)

## Hourly Simulation Data

| Hr | Solar | DG | BESS Pwr | BESS E | SoC% | State | ChgFrom | Load | Supply | Deficit | Sol→Ld | BESS→Ld | DG→Ld | Period | DG Mode |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night | OFF |
| 1 | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0 | Night | OFF |
| 2 | 0 | 27 | 2 | 30.15 | 30.15 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 3 | 0 | 27 | 2 | 31.99 | 31.99 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 4 | 0.57 | 27 | 2.57 | 34.36 | 34.36 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43 | Night | NORMAL |
| 5 | 2.02 | 27 | 4.02 | 38.07 | 38.07 | Charging | DG | 25 | 25 | 0 | 2.02 | 0 | 22.98 | Night | NORMAL |
| 6 | 8.71 | 0 | 10 | 27.22 | 27.22 | Discharging | - | 25 | 18.71 | 6.29 | 8.71 | 10 | 0 | Day | OFF |
| 7 | 10.81 | 0 | 10 | 16.38 | 16.38 | Discharging | - | 25 | 20.81 | 4.19 | 10.81 | 10 | 0 | Day | OFF |
| 8 | 18.77 | 0 | 5.88 | 10 | 10 | Discharging | - | 25 | 24.65 | 0.35 | 18.77 | 5.88 | 0 | Day | OFF |
| 9 | 17.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 17.92 | 7.08 | 17.92 | 0 | 0 | Day | OFF |
| 10 | 21.07 | 0 | 0 | 10 | 10 | Idle | - | 25 | 21.07 | 3.93 | 21.07 | 0 | 0 | Day | OFF |
| 11 | 22.94 | 0 | 0 | 10 | 10 | Idle | - | 25 | 22.94 | 2.06 | 22.94 | 0 | 0 | Day | OFF |
| 12 | 49.85 | 0 | 10 | 19.22 | 19.22 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | OFF |
| 13 | 50.83 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | OFF |
| 14 | 17.66 | 0 | 7.34 | 20.48 | 20.48 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0 | Day | OFF |
| 15 | 5.61 | 0 | 9.66 | 10 | 10 | Discharging | - | 25 | 15.27 | 9.73 | 5.61 | 9.66 | 0 | Day | OFF |
| 16 | 8.52 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.52 | 16.48 | 8.52 | 0 | 0 | Day | OFF |
| 17 | 5.42 | 0 | 0 | 10 | 10 | Idle | - | 25 | 5.42 | 19.58 | 5.42 | 0 | 0 | Day | OFF |
| 18 | 2.43 | 27 | 4.43 | 14.08 | 14.08 | Charging | DG | 25 | 25 | 0 | 2.43 | 0 | 22.57 | Night | NORMAL |
| 19 | 0.73 | 27 | 2.73 | 16.6 | 16.6 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27 | Night | NORMAL |
| 20 | 0 | 27 | 2 | 18.45 | 18.45 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 21 | 0 | 27 | 2 | 20.29 | 20.29 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 22 | 0 | 27 | 2 | 22.13 | 22.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 23 | 0 | 27 | 2 | 23.98 | 23.98 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 0 | 0 | 27 | 2 | 25.82 | 25.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 1 | 0 | 27 | 2 | 27.66 | 27.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 2 | 0 | 27 | 2 | 29.51 | 29.51 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 3 | 0 | 27 | 2 | 31.35 | 31.35 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 4 | 1.25 | 27 | 3.25 | 34.35 | 34.35 | Charging | DG | 25 | 25 | 0 | 1.25 | 0 | 23.75 | Night | NORMAL |
| 5 | 3.35 | 27 | 5.35 | 39.28 | 39.28 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65 | Night | NORMAL |
| 6 | 6.28 | 0 | 10 | 28.43 | 28.43 | Discharging | - | 25 | 16.28 | 8.72 | 6.28 | 10 | 0 | Day | OFF |
| 7 | 12.72 | 0 | 10 | 17.59 | 17.59 | Discharging | - | 25 | 22.72 | 2.28 | 12.72 | 10 | 0 | Day | OFF |
| 8 | 26.88 | 0 | 1.88 | 19.32 | 19.32 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | OFF |
| 9 | 34.82 | 0 | 9.82 | 28.38 | 28.38 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | OFF |
| 10 | 30.45 | 0 | 5.45 | 33.4 | 33.4 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | OFF |
| 11 | 27.44 | 0 | 2.44 | 35.65 | 35.65 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | OFF |
| 12 | 29.18 | 0 | 4.18 | 39.5 | 39.5 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0 | Day | OFF |
| 13 | 12.43 | 0 | 10 | 28.66 | 28.66 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0 | Day | OFF |
| 14 | 15.36 | 0 | 9.64 | 18.2 | 18.2 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0 | Day | OFF |
| 15 | 19.44 | 0 | 5.56 | 12.17 | 12.17 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0 | Day | OFF |
| 16 | 11.92 | 0 | 2 | 10 | 10 | Discharging | - | 25 | 13.92 | 11.08 | 11.92 | 2 | 0 | Day | OFF |
| 17 | 10.96 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.96 | 14.04 | 10.96 | 0 | 0 | Day | OFF |
| 18 | 4.89 | 27 | 6.89 | 16.35 | 16.35 | Charging | DG | 25 | 25 | 0 | 4.89 | 0 | 20.11 | Night | NORMAL |
| 19 | 1.18 | 27 | 3.18 | 19.28 | 19.28 | Charging | DG | 25 | 25 | 0 | 1.18 | 0 | 23.82 | Night | NORMAL |
| 20 | 0 | 27 | 2 | 21.13 | 21.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 21 | 0 | 27 | 2 | 22.97 | 22.97 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 22 | 0 | 27 | 2 | 24.82 | 24.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |
| 23 | 0 | 27 | 2 | 26.66 | 26.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25 | Night | NORMAL |