## Rules
Category | Type | Rule
T0: Solar + BESS Only | Description | Pure green system with no DG. BESS provides backup when solar insufficient.
T0: Solar + BESS Only | Merit Order | Solar → BESS → Unserved
T0: Solar + BESS Only | Dispatch | 1. Solar serves load first (direct priority)
T0: Solar + BESS Only | Dispatch | 2. BESS discharges to cover remaining load after solar
T0: Solar + BESS Only | Dispatch | 3. If BESS depleted (SoC ≤ 10%), load goes unserved
T0: Solar + BESS Only | Dispatch | 4. No DG available in this topology
T0: Solar + BESS Only | Charging | 1. BESS charges ONLY from excess solar (after load served)
T0: Solar + BESS Only | Charging | 2. Charge rate limited by BESS power (10 MW)
T0: Solar + BESS Only | Charging | 3. Charge efficiency: Energy stored = Power × √0.85
T0: Solar + BESS Only | Charging | 4. If BESS full (SoC = 90%), excess solar is curtailed
T0: Solar + BESS Only | Constraint | • BESS cannot charge and discharge in same hour
T0: Solar + BESS Only | Constraint | • SoC bounded: 10% (min) to 90% (max)
T0: Solar + BESS Only | Constraint | • No DG backup - unserved energy if BESS depleted
T1: Green Priority | Description | Maximize green energy. DG activates only when Solar + BESS cannot meet load.
T1: Green Priority | Merit Order | Solar → BESS → DG → Unserved
T1: Green Priority | Dispatch | 1. Solar serves load first (highest priority)
T1: Green Priority | Dispatch | 2. BESS discharges to cover remaining load
T1: Green Priority | Dispatch | 3. DG activates ONLY when Solar + BESS insufficient
T1: Green Priority | Dispatch | 4. DG runs at Full Capacity (27 MW) when ON
T1: Green Priority | Dispatch | 5. DG does NOT turn on proactively to charge BESS
T1: Green Priority | Charging | 1. BESS charges from excess solar (priority 1)
T1: Green Priority | Charging | 2. BESS charges from excess DG when DG running
T1: Green Priority | Charging | 3. Charging only when BESS not discharging
T1: Green Priority | Charging | 4. Charge rate limited by BESS power (10 MW)
T1: Green Priority | Constraint | • BESS cannot charge and discharge in same hour
T1: Green Priority | Constraint | • DG is reactive only - no proactive charging
T1: Green Priority | Constraint | • Green-first: maximize solar/BESS usage
T2: DG Night Charge | Description | DG runs proactively at night to charge BESS. Day is strictly green.
T2: DG Night Charge | Merit Order | Night: DG → BESS ¦ Day: Solar → BESS → Unserved
T2: DG Night Charge | Dispatch | 1. NIGHT (18:00-06:00): DG turns ON when night starts
T2: DG Night Charge | Dispatch | 2. NIGHT: DG serves load, excess charges BESS
T2: DG Night Charge | Dispatch | 3. NIGHT: DG OFF when SoC reaches 80%
T2: DG Night Charge | Dispatch | 4. NIGHT: If DG OFF, BESS discharges to load
T2: DG Night Charge | Dispatch | 5. DAY (06:00-18:00): DG DISABLED
T2: DG Night Charge | Dispatch | 6. DAY: Solar → BESS → Unserved
T2: DG Night Charge | Charging | 1. NIGHT: BESS charges from excess DG
T2: DG Night Charge | Charging | 2. DAY: BESS charges from excess solar only
T2: DG Night Charge | Charging | 3. Charging stops at SoC = 90%
T2: DG Night Charge | Constraint | • DG proactive at night (not SoC-triggered)
T2: DG Night Charge | Constraint | • Day strictly green unless emergency enabled
T2: DG Night Charge | Constraint | • SoC thresholds: ON ≤ 30%, OFF ≥ 80%
T3: DG Blackout Window | Description | DG disabled during blackout hours (noise/emissions). Reactive outside.
T3: DG Blackout Window | Merit Order | Blackout: Solar → BESS → Unserved ¦ Normal: Solar → BESS → DG
T3: DG Blackout Window | Dispatch | 1. BLACKOUT (22:00-06:00): DG strictly DISABLED
T3: DG Blackout Window | Dispatch | 2. BLACKOUT: Solar → BESS → Unserved
T3: DG Blackout Window | Dispatch | 3. OUTSIDE: Solar → BESS → DG → Unserved
T3: DG Blackout Window | Dispatch | 4. DG reactive (only when Solar+BESS insufficient)
T3: DG Blackout Window | Dispatch | 5. DG runs at Full Capacity (27 MW) when ON
T3: DG Blackout Window | Charging | 1. BESS charges from excess solar (always)
T3: DG Blackout Window | Charging | 2. BESS charges from excess DG (outside blackout)
T3: DG Blackout Window | Charging | 3. No DG charging during blackout
T3: DG Blackout Window | Constraint | • DG cannot run during blackout
T3: DG Blackout Window | Constraint | • No emergency override during blackout
T3: DG Blackout Window | Constraint | • BESS must survive blackout hours
T4: DG Emergency Only | Description | SoC-triggered DG with no time restrictions. DG as 'Range Extender'.
T4: DG Emergency Only | Merit Order | DG OFF: Solar → BESS ¦ DG ON: Solar → DG → BESS Assist
T4: DG Emergency Only | Dispatch | 1. Normal: Solar → BESS → Unserved (DG OFF)
T4: DG Emergency Only | Dispatch | 2. DG ON when SoC ≤ 30%
T4: DG Emergency Only | Dispatch | 3. DG OFF when SoC ≥ 80%
T4: DG Emergency Only | Dispatch | 4. ASSIST MODE: DG < Load → BESS assists
T4: DG Emergency Only | Dispatch | 5. RECOVERY MODE: DG ≥ Load → BESS charges
T4: DG Emergency Only | Dispatch | 6. No time restrictions - DG anytime
T4: DG Emergency Only | Charging | 1. BESS charges from excess solar (DG OFF)
T4: DG Emergency Only | Charging | 2. BESS charges from excess DG (Recovery Mode)
T4: DG Emergency Only | Charging | 3. No charging in Assist Mode (discharging)
T4: DG Emergency Only | Constraint | • Deadband: ON ≤ 30%, OFF ≥ 80%
T4: DG Emergency Only | Constraint | • DG SoC-triggered, not load-triggered
T4: DG Emergency Only | Constraint | • Cycle limit monitor-only
T5: DG Day Charge | Description | SoC-triggered DG during day. Night is silent (DG disabled).
T5: DG Day Charge | Merit Order | Day: Solar → DG (if triggered) → BESS ¦ Night: Solar → BESS
T5: DG Day Charge | Dispatch | 1. DAY (06:00-18:00): DG allowed (SoC-triggered)
T5: DG Day Charge | Dispatch | 2. DAY: DG ON ≤ 30%, OFF ≥ 80%
T5: DG Day Charge | Dispatch | 3. DAY: ASSIST when DG < Load, RECOVERY when DG ≥ Load
T5: DG Day Charge | Dispatch | 4. NIGHT (18:00-06:00): DG DISABLED (silent)
T5: DG Day Charge | Dispatch | 5. NIGHT: Solar → BESS → Emergency DG → Unserved
T5: DG Day Charge | Dispatch | 6. SUNSET CUT: DG OFF when night starts
T5: DG Day Charge | Charging | 1. DAY: BESS charges from solar + DG (Recovery)
T5: DG Day Charge | Charging | 2. NIGHT: BESS charges from solar only
T5: DG Day Charge | Charging | 3. No DG charging at night
T5: DG Day Charge | Constraint | • Silent nights for residential areas
T5: DG Day Charge | Constraint | • DG SoC-triggered during day only
T5: DG Day Charge | Constraint | • Cycle limit monitor-only
T6: DG Night SoC Trigger | Description | SoC-triggered DG during night. Day is green (DG disabled).
T6: DG Night SoC Trigger | Merit Order | Night: Solar → DG (if triggered) → BESS ¦ Day: Solar → BESS
T6: DG Night SoC Trigger | Dispatch | 1. NIGHT (18:00-06:00): DG allowed (SoC-triggered)
T6: DG Night SoC Trigger | Dispatch | 2. NIGHT: DG ON ≤ 30%, OFF ≥ 80%
T6: DG Night SoC Trigger | Dispatch | 3. NIGHT: ASSIST when DG < Load, RECOVERY when DG ≥ Load
T6: DG Night SoC Trigger | Dispatch | 4. DAY (06:00-18:00): DG DISABLED (green)
T6: DG Night SoC Trigger | Dispatch | 5. DAY: Solar → BESS → Emergency DG → Unserved
T6: DG Night SoC Trigger | Dispatch | 6. SUNRISE CUT: DG OFF when day starts
T6: DG Night SoC Trigger | Charging | 1. NIGHT: BESS charges from DG (Recovery Mode)
T6: DG Night SoC Trigger | Charging | 2. DAY: BESS charges from solar only
T6: DG Night SoC Trigger | Charging | 3. No DG charging during day
T6: DG Night SoC Trigger | Constraint | • Green days maximize solar
T6: DG Night SoC Trigger | Constraint | • DG runs only at night for recharge
T6: DG Night SoC Trigger | Constraint | • Cycle limit enforcement allowed

## T0_Solar_BESS
Hour | Day | Solar_MW | DG_MW | BESS_Power_MW | BESS_Energy_MWh | SoC_% | BESS_State | Charge_From | Load_MW | Total_Supply_MW | Deficit_MW | Solar_to_Load_MW | BESS_to_Load_MW | DG_to_Load_MW
0 | 1 | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
1 | 1 | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
2 | 1 | 0 | 0 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
3 | 1 | 0 | 0 | 6.88 | 10 | 10 | Discharging | - | 25 | 6.88 | 18.12 | 0 | 6.88 | 0
4 | 1 | 0.57 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.57 | 24.43 | 0.57 | 0 | 0
5 | 1 | 2.02 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.02 | 22.98 | 2.02 | 0 | 0
6 | 1 | 8.71 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.71 | 16.29 | 8.71 | 0 | 0
7 | 1 | 10.81 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.81 | 14.19 | 10.81 | 0 | 0
8 | 1 | 18.77 | 0 | 0 | 10 | 10 | Idle | - | 25 | 18.77 | 6.23 | 18.77 | 0 | 0
9 | 1 | 17.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 17.92 | 7.08 | 17.92 | 0 | 0
10 | 1 | 21.07 | 0 | 0 | 10 | 10 | Idle | - | 25 | 21.07 | 3.93 | 21.07 | 0 | 0
11 | 1 | 22.94 | 0 | 0 | 10 | 10 | Idle | - | 25 | 22.94 | 2.06 | 22.94 | 0 | 0
12 | 1 | 49.85 | 0 | 10 | 19.22 | 19.22 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 1 | 50.83 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
14 | 1 | 17.66 | 0 | 7.34 | 20.48 | 20.48 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0
15 | 1 | 5.61 | 0 | 9.66 | 10 | 10 | Discharging | - | 25 | 15.27 | 9.73 | 5.61 | 9.66 | 0
16 | 1 | 8.52 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.52 | 16.48 | 8.52 | 0 | 0
17 | 1 | 5.42 | 0 | 0 | 10 | 10 | Idle | - | 25 | 5.42 | 19.58 | 5.42 | 0 | 0
18 | 1 | 2.43 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.43 | 22.57 | 2.43 | 0 | 0
19 | 1 | 0.73 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.73 | 24.27 | 0.73 | 0 | 0
20 | 1 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
21 | 1 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
22 | 1 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
23 | 1 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
0 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
1 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
2 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
3 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
4 | 2 | 1.25 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.25 | 23.75 | 1.25 | 0 | 0
5 | 2 | 3.35 | 0 | 0 | 10 | 10 | Idle | - | 25 | 3.35 | 21.65 | 3.35 | 0 | 0
6 | 2 | 6.28 | 0 | 0 | 10 | 10 | Idle | - | 25 | 6.28 | 18.72 | 6.28 | 0 | 0
7 | 2 | 12.72 | 0 | 0 | 10 | 10 | Idle | - | 25 | 12.72 | 12.28 | 12.72 | 0 | 0
8 | 2 | 26.88 | 0 | 1.88 | 11.73 | 11.73 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
9 | 2 | 34.82 | 0 | 9.82 | 20.79 | 20.79 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
10 | 2 | 30.45 | 0 | 5.45 | 25.81 | 25.81 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
11 | 2 | 27.44 | 0 | 2.44 | 28.06 | 28.06 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
12 | 2 | 29.18 | 0 | 4.18 | 31.91 | 31.91 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 2 | 12.43 | 0 | 10 | 21.07 | 21.07 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0
14 | 2 | 15.36 | 0 | 9.64 | 10.61 | 10.61 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0
15 | 2 | 19.44 | 0 | 0.56 | 10 | 10 | Discharging | - | 25 | 20 | 5 | 19.44 | 0.56 | 0
16 | 2 | 11.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 11.92 | 13.08 | 11.92 | 0 | 0
17 | 2 | 10.96 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.96 | 14.04 | 10.96 | 0 | 0
18 | 2 | 4.89 | 0 | 0 | 10 | 10 | Idle | - | 25 | 4.89 | 20.11 | 4.89 | 0 | 0
19 | 2 | 1.18 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.18 | 23.82 | 1.18 | 0 | 0
20 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
21 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
22 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
23 | 2 | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0

## T1_Green_Priority
Hour | Day | Solar_MW | DG_MW | BESS_Power_MW | BESS_Energy_MWh | SoC_% | BESS_State | Charge_From | Load_MW | Total_Supply_MW | Deficit_MW | Solar_to_Load_MW | BESS_to_Load_MW | DG_to_Load_MW
0 | 1 | 0 | 27 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 25 | 0 | 0 | 10 | 15
1 | 1 | 0 | 27 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 25 | 0 | 0 | 10 | 15
2 | 1 | 0 | 27 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 25 | 0 | 0 | 10 | 15
3 | 1 | 0 | 27 | 6.88 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 6.88 | 18.12
4 | 1 | 0.57 | 27 | 2.57 | 12.37 | 12.37 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43
5 | 1 | 2.02 | 27 | 2.18 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 2.02 | 2.18 | 20.8
6 | 1 | 8.71 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 8.71 | 0 | 16.29
7 | 1 | 10.81 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 10.81 | 8.5 | 5.69
8 | 1 | 18.77 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 18.77 | 0 | 6.23
9 | 1 | 17.92 | 0 | 7.08 | 11.54 | 11.54 | Discharging | - | 25 | 25 | 0 | 17.92 | 7.08 | 0
10 | 1 | 21.07 | 27 | 1.42 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 21.07 | 1.42 | 2.51
11 | 1 | 22.94 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 22.94 | 0 | 2.06
12 | 1 | 49.85 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 1 | 50.83 | 0 | 10 | 37.66 | 37.66 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
14 | 1 | 17.66 | 0 | 7.34 | 29.7 | 29.7 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0
15 | 1 | 5.61 | 27 | 10 | 18.85 | 18.85 | Discharging | - | 25 | 25 | 0 | 5.61 | 10 | 9.39
16 | 1 | 8.52 | 27 | 8.16 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 8.52 | 8.16 | 8.32
17 | 1 | 5.42 | 27 | 7.42 | 16.84 | 16.84 | Charging | DG | 25 | 25 | 0 | 5.42 | 0 | 19.58
18 | 1 | 2.43 | 27 | 6.31 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 2.43 | 6.31 | 16.26
19 | 1 | 0.73 | 27 | 2.73 | 12.52 | 12.52 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27
20 | 1 | 0 | 27 | 2.32 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 2.32 | 22.68
21 | 1 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 1 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3
23 | 1 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
0 | 2 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3
1 | 2 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
2 | 2 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3
3 | 2 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
4 | 2 | 1.25 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 1.25 | 1.7 | 22.05
5 | 2 | 3.35 | 27 | 5.35 | 14.93 | 14.93 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65
6 | 2 | 6.28 | 27 | 4.55 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 6.28 | 4.55 | 14.17
7 | 2 | 12.72 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 12.72 | 0 | 12.28
8 | 2 | 26.88 | 0 | 1.88 | 20.95 | 20.95 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
9 | 2 | 34.82 | 0 | 9.82 | 30.01 | 30.01 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
10 | 2 | 30.45 | 0 | 5.45 | 35.03 | 35.03 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
11 | 2 | 27.44 | 0 | 2.44 | 37.28 | 37.28 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
12 | 2 | 29.18 | 0 | 4.18 | 41.13 | 41.13 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 2 | 12.43 | 27 | 10 | 30.29 | 30.29 | Discharging | - | 25 | 25 | 0 | 12.43 | 10 | 2.57
14 | 2 | 15.36 | 0 | 9.64 | 19.83 | 19.83 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0
15 | 2 | 19.44 | 0 | 5.56 | 13.8 | 13.8 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0
16 | 2 | 11.92 | 27 | 3.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 11.92 | 3.5 | 9.58
17 | 2 | 10.96 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 10.96 | 0 | 14.04
18 | 2 | 4.89 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 4.89 | 8.5 | 11.61
19 | 2 | 1.18 | 27 | 3.18 | 12.93 | 12.93 | Charging | DG | 25 | 25 | 0 | 1.18 | 0 | 23.82
20 | 2 | 0 | 27 | 2.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 2.7 | 22.3
21 | 2 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 2 | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3
23 | 2 | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25

## T2_DG_Night_Charge
Hour | Day | Period | Solar_MW | DG_MW | BESS_Power_MW | BESS_Energy_MWh | SoC_% | BESS_State | Charge_From | Load_MW | Total_Supply_MW | Deficit_MW | Solar_to_Load_MW | BESS_to_Load_MW | DG_to_Load_MW
0 | 1 | Night | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
1 | 1 | Night | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
2 | 1 | Night | 0 | 27 | 2 | 30.15 | 30.15 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
3 | 1 | Night | 0 | 27 | 2 | 31.99 | 31.99 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
4 | 1 | Night | 0.57 | 27 | 2.57 | 34.36 | 34.36 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43
5 | 1 | Night | 2.02 | 27 | 4.02 | 38.07 | 38.07 | Charging | DG | 25 | 25 | 0 | 2.02 | 0 | 22.98
6 | 1 | Day | 8.71 | 0 | 10 | 27.22 | 27.22 | Discharging | - | 25 | 18.71 | 6.29 | 8.71 | 10 | 0
7 | 1 | Day | 10.81 | 0 | 10 | 16.38 | 16.38 | Discharging | - | 25 | 20.81 | 4.19 | 10.81 | 10 | 0
8 | 1 | Day | 18.77 | 0 | 5.88 | 10 | 10 | Discharging | - | 25 | 24.65 | 0.35 | 18.77 | 5.88 | 0
9 | 1 | Day | 17.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 17.92 | 7.08 | 17.92 | 0 | 0
10 | 1 | Day | 21.07 | 0 | 0 | 10 | 10 | Idle | - | 25 | 21.07 | 3.93 | 21.07 | 0 | 0
11 | 1 | Day | 22.94 | 0 | 0 | 10 | 10 | Idle | - | 25 | 22.94 | 2.06 | 22.94 | 0 | 0
12 | 1 | Day | 49.85 | 0 | 10 | 19.22 | 19.22 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 1 | Day | 50.83 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
14 | 1 | Day | 17.66 | 0 | 7.34 | 20.48 | 20.48 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0
15 | 1 | Day | 5.61 | 0 | 9.66 | 10 | 10 | Discharging | - | 25 | 15.27 | 9.73 | 5.61 | 9.66 | 0
16 | 1 | Day | 8.52 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.52 | 16.48 | 8.52 | 0 | 0
17 | 1 | Day | 5.42 | 0 | 0 | 10 | 10 | Idle | - | 25 | 5.42 | 19.58 | 5.42 | 0 | 0
18 | 1 | Night | 2.43 | 27 | 4.43 | 14.08 | 14.08 | Charging | DG | 25 | 25 | 0 | 2.43 | 0 | 22.57
19 | 1 | Night | 0.73 | 27 | 2.73 | 16.6 | 16.6 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27
20 | 1 | Night | 0 | 27 | 2 | 18.45 | 18.45 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
21 | 1 | Night | 0 | 27 | 2 | 20.29 | 20.29 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 1 | Night | 0 | 27 | 2 | 22.13 | 22.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
23 | 1 | Night | 0 | 27 | 2 | 23.98 | 23.98 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
0 | 2 | Night | 0 | 27 | 2 | 25.82 | 25.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
1 | 2 | Night | 0 | 27 | 2 | 27.66 | 27.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
2 | 2 | Night | 0 | 27 | 2 | 29.51 | 29.51 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
3 | 2 | Night | 0 | 27 | 2 | 31.35 | 31.35 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
4 | 2 | Night | 1.25 | 27 | 3.25 | 34.35 | 34.35 | Charging | DG | 25 | 25 | 0 | 1.25 | 0 | 23.75
5 | 2 | Night | 3.35 | 27 | 5.35 | 39.28 | 39.28 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65
6 | 2 | Day | 6.28 | 0 | 10 | 28.43 | 28.43 | Discharging | - | 25 | 16.28 | 8.72 | 6.28 | 10 | 0
7 | 2 | Day | 12.72 | 0 | 10 | 17.59 | 17.59 | Discharging | - | 25 | 22.72 | 2.28 | 12.72 | 10 | 0
8 | 2 | Day | 26.88 | 0 | 1.88 | 19.32 | 19.32 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
9 | 2 | Day | 34.82 | 0 | 9.82 | 28.38 | 28.38 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
10 | 2 | Day | 30.45 | 0 | 5.45 | 33.4 | 33.4 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
11 | 2 | Day | 27.44 | 0 | 2.44 | 35.65 | 35.65 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
12 | 2 | Day | 29.18 | 0 | 4.18 | 39.5 | 39.5 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 2 | Day | 12.43 | 0 | 10 | 28.66 | 28.66 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0
14 | 2 | Day | 15.36 | 0 | 9.64 | 18.2 | 18.2 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0
15 | 2 | Day | 19.44 | 0 | 5.56 | 12.17 | 12.17 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0
16 | 2 | Day | 11.92 | 0 | 2 | 10 | 10 | Discharging | - | 25 | 13.92 | 11.08 | 11.92 | 2 | 0
17 | 2 | Day | 10.96 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.96 | 14.04 | 10.96 | 0 | 0
18 | 2 | Night | 4.89 | 27 | 6.89 | 16.35 | 16.35 | Charging | DG | 25 | 25 | 0 | 4.89 | 0 | 20.11
19 | 2 | Night | 1.18 | 27 | 3.18 | 19.28 | 19.28 | Charging | DG | 25 | 25 | 0 | 1.18 | 0 | 23.82
20 | 2 | Night | 0 | 27 | 2 | 21.13 | 21.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
21 | 2 | Night | 0 | 27 | 2 | 22.97 | 22.97 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 2 | Night | 0 | 27 | 2 | 24.82 | 24.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
23 | 2 | Night | 0 | 27 | 2 | 26.66 | 26.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25

## T3_DG_Blackout
Hour | Day | Period | Solar_MW | DG_MW | BESS_Power_MW | BESS_Energy_MWh | SoC_% | BESS_State | Charge_From | Load_MW | Total_Supply_MW | Deficit_MW | Solar_to_Load_MW | BESS_to_Load_MW | DG_to_Load_MW
0 | 1 | Blackout | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
1 | 1 | Blackout | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
2 | 1 | Blackout | 0 | 0 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
3 | 1 | Blackout | 0 | 0 | 6.88 | 10 | 10 | Discharging | - | 25 | 6.88 | 18.12 | 0 | 6.88 | 0
4 | 1 | Blackout | 0.57 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.57 | 24.43 | 0.57 | 0 | 0
5 | 1 | Blackout | 2.02 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.02 | 22.98 | 2.02 | 0 | 0
6 | 1 | Normal | 8.71 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 8.71 | 0 | 16.29
7 | 1 | Normal | 10.81 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 10.81 | 8.5 | 5.69
8 | 1 | Normal | 18.77 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 18.77 | 0 | 6.23
9 | 1 | Normal | 17.92 | 0 | 7.08 | 11.54 | 11.54 | Discharging | - | 25 | 25 | 0 | 17.92 | 7.08 | 0
10 | 1 | Normal | 21.07 | 27 | 1.42 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 21.07 | 1.42 | 2.51
11 | 1 | Normal | 22.94 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 22.94 | 0 | 2.06
12 | 1 | Normal | 49.85 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 1 | Normal | 50.83 | 0 | 10 | 37.66 | 37.66 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
14 | 1 | Normal | 17.66 | 0 | 7.34 | 29.7 | 29.7 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0
15 | 1 | Normal | 5.61 | 27 | 10 | 18.85 | 18.85 | Discharging | - | 25 | 25 | 0 | 5.61 | 10 | 9.39
16 | 1 | Normal | 8.52 | 27 | 8.16 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 8.52 | 8.16 | 8.32
17 | 1 | Normal | 5.42 | 27 | 7.42 | 16.84 | 16.84 | Charging | DG | 25 | 25 | 0 | 5.42 | 0 | 19.58
18 | 1 | Normal | 2.43 | 27 | 6.31 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 2.43 | 6.31 | 16.26
19 | 1 | Normal | 0.73 | 27 | 2.73 | 12.52 | 12.52 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27
20 | 1 | Normal | 0 | 27 | 2.32 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 2.32 | 22.68
21 | 1 | Normal | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 1 | Blackout | 0 | 0 | 1.7 | 10 | 10 | Discharging | - | 25 | 1.7 | 23.3 | 0 | 1.7 | 0
23 | 1 | Blackout | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
0 | 2 | Blackout | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
1 | 2 | Blackout | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
2 | 2 | Blackout | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
3 | 2 | Blackout | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
4 | 2 | Blackout | 1.25 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.25 | 23.75 | 1.25 | 0 | 0
5 | 2 | Blackout | 3.35 | 0 | 0 | 10 | 10 | Idle | - | 25 | 3.35 | 21.65 | 3.35 | 0 | 0
6 | 2 | Normal | 6.28 | 27 | 8.28 | 17.63 | 17.63 | Charging | DG | 25 | 25 | 0 | 6.28 | 0 | 18.72
7 | 2 | Normal | 12.72 | 27 | 7.04 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 12.72 | 7.04 | 5.24
8 | 2 | Normal | 26.88 | 0 | 1.88 | 11.73 | 11.73 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
9 | 2 | Normal | 34.82 | 0 | 9.82 | 20.79 | 20.79 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
10 | 2 | Normal | 30.45 | 0 | 5.45 | 25.81 | 25.81 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
11 | 2 | Normal | 27.44 | 0 | 2.44 | 28.06 | 28.06 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
12 | 2 | Normal | 29.18 | 0 | 4.18 | 31.91 | 31.91 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 2 | Normal | 12.43 | 27 | 10 | 21.07 | 21.07 | Discharging | - | 25 | 25 | 0 | 12.43 | 10 | 2.57
14 | 2 | Normal | 15.36 | 0 | 9.64 | 10.61 | 10.61 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0
15 | 2 | Normal | 19.44 | 27 | 0.56 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 19.44 | 0.56 | 5
16 | 2 | Normal | 11.92 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 11.92 | 0 | 13.08
17 | 2 | Normal | 10.96 | 27 | 8.5 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 10.96 | 8.5 | 5.54
18 | 2 | Normal | 4.89 | 27 | 6.89 | 16.35 | 16.35 | Charging | DG | 25 | 25 | 0 | 4.89 | 0 | 20.11
19 | 2 | Normal | 1.18 | 27 | 5.86 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 1.18 | 5.86 | 17.96
20 | 2 | Normal | 0 | 27 | 2 | 11.84 | 11.84 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
21 | 2 | Normal | 0 | 27 | 1.7 | 10 | 10 | Discharging | - | 25 | 25 | 0 | 0 | 1.7 | 23.3
22 | 2 | Blackout | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
23 | 2 | Blackout | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0

## T4_DG_Emergency
Hour | Day | DG_Mode | Solar_MW | DG_MW | BESS_Power_MW | BESS_Energy_MWh | SoC_% | BESS_State | Charge_From | Load_MW | Total_Supply_MW | Deficit_MW | Solar_to_Load_MW | BESS_to_Load_MW | DG_to_Load_MW
0 | 1 | OFF | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
1 | 1 | OFF | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
2 | 1 | ON-Recovery | 0 | 27 | 2 | 30.15 | 30.15 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
3 | 1 | ON-Recovery | 0 | 27 | 2 | 31.99 | 31.99 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
4 | 1 | ON-Recovery | 0.57 | 27 | 2.57 | 34.36 | 34.36 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43
5 | 1 | ON-Recovery | 2.02 | 27 | 4.02 | 38.07 | 38.07 | Charging | DG | 25 | 25 | 0 | 2.02 | 0 | 22.98
6 | 1 | ON-Recovery | 8.71 | 27 | 10 | 47.29 | 47.29 | Charging | DG | 25 | 25 | 0 | 8.71 | 0 | 16.29
7 | 1 | ON-Recovery | 10.81 | 27 | 10 | 56.51 | 56.51 | Charging | DG | 25 | 25 | 0 | 10.81 | 0 | 14.19
8 | 1 | ON-Recovery | 18.77 | 27 | 10 | 65.73 | 65.73 | Charging | DG | 25 | 25 | 0 | 18.77 | 0 | 6.23
9 | 1 | ON-Recovery | 17.92 | 27 | 10 | 74.95 | 74.95 | Charging | DG | 25 | 25 | 0 | 17.92 | 0 | 7.08
10 | 1 | ON-Recovery | 21.07 | 27 | 10 | 84.17 | 84.17 | Charging | DG | 25 | 25 | 0 | 21.07 | 0 | 3.93
11 | 1 | OFF | 22.94 | 0 | 2.06 | 81.93 | 81.93 | Discharging | - | 25 | 25 | 0 | 22.94 | 2.06 | 0
12 | 1 | OFF | 49.85 | 0 | 8.75 | 90 | 90 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 1 | OFF | 50.83 | 0 | 0 | 90 | 90 | Idle | - | 25 | 25 | 0 | 25 | 0 | 0
14 | 1 | OFF | 17.66 | 0 | 7.34 | 82.04 | 82.04 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0
15 | 1 | OFF | 5.61 | 0 | 10 | 71.19 | 71.19 | Discharging | - | 25 | 15.61 | 9.39 | 5.61 | 10 | 0
16 | 1 | OFF | 8.52 | 0 | 10 | 60.35 | 60.35 | Discharging | - | 25 | 18.52 | 6.48 | 8.52 | 10 | 0
17 | 1 | OFF | 5.42 | 0 | 10 | 49.5 | 49.5 | Discharging | - | 25 | 15.42 | 9.58 | 5.42 | 10 | 0
18 | 1 | OFF | 2.43 | 0 | 10 | 38.65 | 38.65 | Discharging | - | 25 | 12.43 | 12.57 | 2.43 | 10 | 0
19 | 1 | OFF | 0.73 | 0 | 10 | 27.81 | 27.81 | Discharging | - | 25 | 10.73 | 14.27 | 0.73 | 10 | 0
20 | 1 | ON-Recovery | 0 | 27 | 2 | 29.65 | 29.65 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
21 | 1 | ON-Recovery | 0 | 27 | 2 | 31.49 | 31.49 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 1 | ON-Recovery | 0 | 27 | 2 | 33.34 | 33.34 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
23 | 1 | ON-Recovery | 0 | 27 | 2 | 35.18 | 35.18 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
0 | 2 | ON-Recovery | 0 | 27 | 2 | 37.03 | 37.03 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
1 | 2 | ON-Recovery | 0 | 27 | 2 | 38.87 | 38.87 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
2 | 2 | ON-Recovery | 0 | 27 | 2 | 40.71 | 40.71 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
3 | 2 | ON-Recovery | 0 | 27 | 2 | 42.56 | 42.56 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
4 | 2 | ON-Recovery | 1.25 | 27 | 3.25 | 45.55 | 45.55 | Charging | DG | 25 | 25 | 0 | 1.25 | 0 | 23.75
5 | 2 | ON-Recovery | 3.35 | 27 | 5.35 | 50.49 | 50.49 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65
6 | 2 | ON-Recovery | 6.28 | 27 | 8.28 | 58.12 | 58.12 | Charging | DG | 25 | 25 | 0 | 6.28 | 0 | 18.72
7 | 2 | ON-Recovery | 12.72 | 27 | 10 | 67.34 | 67.34 | Charging | DG | 25 | 25 | 0 | 12.72 | 0 | 12.28
8 | 2 | ON-Recovery | 26.88 | 27 | 10 | 76.56 | 76.56 | Charging | DG | 25 | 25 | 0 | 25 | 0 | 0
9 | 2 | ON-Recovery | 34.82 | 27 | 10 | 85.78 | 85.78 | Charging | DG | 25 | 25 | 0 | 25 | 0 | 0
10 | 2 | OFF | 30.45 | 0 | 4.58 | 90 | 90 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
11 | 2 | OFF | 27.44 | 0 | 0 | 90 | 90 | Idle | - | 25 | 25 | 0 | 25 | 0 | 0
12 | 2 | OFF | 29.18 | 0 | 0 | 90 | 90 | Idle | - | 25 | 25 | 0 | 25 | 0 | 0
13 | 2 | OFF | 12.43 | 0 | 10 | 79.15 | 79.15 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0
14 | 2 | OFF | 15.36 | 0 | 9.64 | 68.7 | 68.7 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0
15 | 2 | OFF | 19.44 | 0 | 5.56 | 62.67 | 62.67 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0
16 | 2 | OFF | 11.92 | 0 | 10 | 51.82 | 51.82 | Discharging | - | 25 | 21.92 | 3.08 | 11.92 | 10 | 0
17 | 2 | OFF | 10.96 | 0 | 10 | 40.97 | 40.97 | Discharging | - | 25 | 20.96 | 4.04 | 10.96 | 10 | 0
18 | 2 | OFF | 4.89 | 0 | 10 | 30.13 | 30.13 | Discharging | - | 25 | 14.89 | 10.11 | 4.89 | 10 | 0
19 | 2 | OFF | 1.18 | 0 | 10 | 19.28 | 19.28 | Discharging | - | 25 | 11.18 | 13.82 | 1.18 | 10 | 0
20 | 2 | ON-Recovery | 0 | 27 | 2 | 21.12 | 21.12 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
21 | 2 | ON-Recovery | 0 | 27 | 2 | 22.97 | 22.97 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 2 | ON-Recovery | 0 | 27 | 2 | 24.81 | 24.81 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
23 | 2 | ON-Recovery | 0 | 27 | 2 | 26.66 | 26.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25

## T5_DG_Day_Charge
Hour | Day | Period | DG_Mode | Solar_MW | DG_MW | BESS_Power_MW | BESS_Energy_MWh | SoC_% | BESS_State | Charge_From | Load_MW | Total_Supply_MW | Deficit_MW | Solar_to_Load_MW | BESS_to_Load_MW | DG_to_Load_MW
0 | 1 | Night | OFF | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
1 | 1 | Night | OFF | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
2 | 1 | Night | OFF | 0 | 0 | 10 | 17.46 | 17.46 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
3 | 1 | Night | OFF | 0 | 0 | 6.88 | 10 | 10 | Discharging | - | 25 | 6.88 | 18.12 | 0 | 6.88 | 0
4 | 1 | Night | OFF | 0.57 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0.57 | 24.43 | 0.57 | 0 | 0
5 | 1 | Night | OFF | 2.02 | 0 | 0 | 10 | 10 | Idle | - | 25 | 2.02 | 22.98 | 2.02 | 0 | 0
6 | 1 | Day | NORMAL | 8.71 | 27 | 10 | 19.22 | 19.22 | Charging | DG | 25 | 25 | 0 | 8.71 | 0 | 16.29
7 | 1 | Day | NORMAL | 10.81 | 27 | 10 | 28.44 | 28.44 | Charging | DG | 25 | 25 | 0 | 10.81 | 0 | 14.19
8 | 1 | Day | NORMAL | 18.77 | 27 | 10 | 37.66 | 37.66 | Charging | DG | 25 | 25 | 0 | 18.77 | 0 | 6.23
9 | 1 | Day | NORMAL | 17.92 | 27 | 10 | 46.88 | 46.88 | Charging | DG | 25 | 25 | 0 | 17.92 | 0 | 7.08
10 | 1 | Day | NORMAL | 21.07 | 27 | 10 | 56.1 | 56.1 | Charging | DG | 25 | 25 | 0 | 21.07 | 0 | 3.93
11 | 1 | Day | NORMAL | 22.94 | 27 | 10 | 65.32 | 65.32 | Charging | DG | 25 | 25 | 0 | 22.94 | 0 | 2.06
12 | 1 | Day | NORMAL | 49.85 | 27 | 10 | 74.54 | 74.54 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 1 | Day | NORMAL | 50.83 | 27 | 10 | 83.76 | 83.76 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
14 | 1 | Day | OFF | 17.66 | 0 | 7.34 | 75.8 | 75.8 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0
15 | 1 | Day | OFF | 5.61 | 0 | 10 | 64.95 | 64.95 | Discharging | - | 25 | 15.61 | 9.39 | 5.61 | 10 | 0
16 | 1 | Day | OFF | 8.52 | 0 | 10 | 54.1 | 54.1 | Discharging | - | 25 | 18.52 | 6.48 | 8.52 | 10 | 0
17 | 1 | Day | OFF | 5.42 | 0 | 10 | 43.26 | 43.26 | Discharging | - | 25 | 15.42 | 9.58 | 5.42 | 10 | 0
18 | 1 | Night | OFF | 2.43 | 0 | 10 | 32.41 | 32.41 | Discharging | - | 25 | 12.43 | 12.57 | 2.43 | 10 | 0
19 | 1 | Night | OFF | 0.73 | 0 | 10 | 21.56 | 21.56 | Discharging | - | 25 | 10.73 | 14.27 | 0.73 | 10 | 0
20 | 1 | Night | OFF | 0 | 0 | 10 | 10.72 | 10.72 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
21 | 1 | Night | OFF | 0 | 0 | 0.66 | 10 | 10 | Discharging | - | 25 | 0.66 | 24.34 | 0 | 0.66 | 0
22 | 1 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
23 | 1 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
0 | 2 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
1 | 2 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
2 | 2 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
3 | 2 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
4 | 2 | Night | OFF | 1.25 | 0 | 0 | 10 | 10 | Idle | - | 25 | 1.25 | 23.75 | 1.25 | 0 | 0
5 | 2 | Night | OFF | 3.35 | 0 | 0 | 10 | 10 | Idle | - | 25 | 3.35 | 21.65 | 3.35 | 0 | 0
6 | 2 | Day | NORMAL | 6.28 | 27 | 8.28 | 17.63 | 17.63 | Charging | DG | 25 | 25 | 0 | 6.28 | 0 | 18.72
7 | 2 | Day | NORMAL | 12.72 | 27 | 10 | 26.85 | 26.85 | Charging | DG | 25 | 25 | 0 | 12.72 | 0 | 12.28
8 | 2 | Day | NORMAL | 26.88 | 27 | 10 | 36.07 | 36.07 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0
9 | 2 | Day | NORMAL | 34.82 | 27 | 10 | 45.29 | 45.29 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0
10 | 2 | Day | NORMAL | 30.45 | 27 | 10 | 54.51 | 54.51 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0
11 | 2 | Day | NORMAL | 27.44 | 27 | 10 | 63.73 | 63.73 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0
12 | 2 | Day | NORMAL | 29.18 | 27 | 10 | 72.95 | 72.95 | Charging | Solar+DG | 25 | 25 | 0 | 25 | 0 | 0
13 | 2 | Day | NORMAL | 12.43 | 27 | 10 | 82.17 | 82.17 | Charging | DG | 25 | 25 | 0 | 12.43 | 0 | 12.57
14 | 2 | Day | OFF | 15.36 | 0 | 9.64 | 71.71 | 71.71 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0
15 | 2 | Day | OFF | 19.44 | 0 | 5.56 | 65.68 | 65.68 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0
16 | 2 | Day | OFF | 11.92 | 0 | 10 | 54.84 | 54.84 | Discharging | - | 25 | 21.92 | 3.08 | 11.92 | 10 | 0
17 | 2 | Day | OFF | 10.96 | 0 | 10 | 43.99 | 43.99 | Discharging | - | 25 | 20.96 | 4.04 | 10.96 | 10 | 0
18 | 2 | Night | OFF | 4.89 | 0 | 10 | 33.14 | 33.14 | Discharging | - | 25 | 14.89 | 10.11 | 4.89 | 10 | 0
19 | 2 | Night | OFF | 1.18 | 0 | 10 | 22.3 | 22.3 | Discharging | - | 25 | 11.18 | 13.82 | 1.18 | 10 | 0
20 | 2 | Night | OFF | 0 | 0 | 10 | 11.45 | 11.45 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
21 | 2 | Night | OFF | 0 | 0 | 1.34 | 10 | 10 | Discharging | - | 25 | 1.34 | 23.66 | 0 | 1.34 | 0
22 | 2 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0
23 | 2 | Night | OFF | 0 | 0 | 0 | 10 | 10 | Idle | - | 25 | 0 | 25 | 0 | 0 | 0

## T6_DG_Night_SoC
Hour | Day | Period | DG_Mode | Solar_MW | DG_MW | BESS_Power_MW | BESS_Energy_MWh | SoC_% | BESS_State | Charge_From | Load_MW | Total_Supply_MW | Deficit_MW | Solar_to_Load_MW | BESS_to_Load_MW | DG_to_Load_MW
0 | 1 | Night | OFF | 0 | 0 | 10 | 39.15 | 39.15 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
1 | 1 | Night | OFF | 0 | 0 | 10 | 28.31 | 28.31 | Discharging | - | 25 | 10 | 15 | 0 | 10 | 0
2 | 1 | Night | NORMAL | 0 | 27 | 2 | 30.15 | 30.15 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
3 | 1 | Night | NORMAL | 0 | 27 | 2 | 31.99 | 31.99 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
4 | 1 | Night | NORMAL | 0.57 | 27 | 2.57 | 34.36 | 34.36 | Charging | DG | 25 | 25 | 0 | 0.57 | 0 | 24.43
5 | 1 | Night | NORMAL | 2.02 | 27 | 4.02 | 38.07 | 38.07 | Charging | DG | 25 | 25 | 0 | 2.02 | 0 | 22.98
6 | 1 | Day | OFF | 8.71 | 0 | 10 | 27.22 | 27.22 | Discharging | - | 25 | 18.71 | 6.29 | 8.71 | 10 | 0
7 | 1 | Day | OFF | 10.81 | 0 | 10 | 16.38 | 16.38 | Discharging | - | 25 | 20.81 | 4.19 | 10.81 | 10 | 0
8 | 1 | Day | OFF | 18.77 | 0 | 5.88 | 10 | 10 | Discharging | - | 25 | 24.65 | 0.35 | 18.77 | 5.88 | 0
9 | 1 | Day | OFF | 17.92 | 0 | 0 | 10 | 10 | Idle | - | 25 | 17.92 | 7.08 | 17.92 | 0 | 0
10 | 1 | Day | OFF | 21.07 | 0 | 0 | 10 | 10 | Idle | - | 25 | 21.07 | 3.93 | 21.07 | 0 | 0
11 | 1 | Day | OFF | 22.94 | 0 | 0 | 10 | 10 | Idle | - | 25 | 22.94 | 2.06 | 22.94 | 0 | 0
12 | 1 | Day | OFF | 49.85 | 0 | 10 | 19.22 | 19.22 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 1 | Day | OFF | 50.83 | 0 | 10 | 28.44 | 28.44 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
14 | 1 | Day | OFF | 17.66 | 0 | 7.34 | 20.48 | 20.48 | Discharging | - | 25 | 25 | 0 | 17.66 | 7.34 | 0
15 | 1 | Day | OFF | 5.61 | 0 | 9.66 | 10 | 10 | Discharging | - | 25 | 15.27 | 9.73 | 5.61 | 9.66 | 0
16 | 1 | Day | OFF | 8.52 | 0 | 0 | 10 | 10 | Idle | - | 25 | 8.52 | 16.48 | 8.52 | 0 | 0
17 | 1 | Day | OFF | 5.42 | 0 | 0 | 10 | 10 | Idle | - | 25 | 5.42 | 19.58 | 5.42 | 0 | 0
18 | 1 | Night | NORMAL | 2.43 | 27 | 4.43 | 14.08 | 14.08 | Charging | DG | 25 | 25 | 0 | 2.43 | 0 | 22.57
19 | 1 | Night | NORMAL | 0.73 | 27 | 2.73 | 16.6 | 16.6 | Charging | DG | 25 | 25 | 0 | 0.73 | 0 | 24.27
20 | 1 | Night | NORMAL | 0 | 27 | 2 | 18.45 | 18.45 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
21 | 1 | Night | NORMAL | 0 | 27 | 2 | 20.29 | 20.29 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 1 | Night | NORMAL | 0 | 27 | 2 | 22.13 | 22.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
23 | 1 | Night | NORMAL | 0 | 27 | 2 | 23.98 | 23.98 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
0 | 2 | Night | NORMAL | 0 | 27 | 2 | 25.82 | 25.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
1 | 2 | Night | NORMAL | 0 | 27 | 2 | 27.66 | 27.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
2 | 2 | Night | NORMAL | 0 | 27 | 2 | 29.51 | 29.51 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
3 | 2 | Night | NORMAL | 0 | 27 | 2 | 31.35 | 31.35 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
4 | 2 | Night | NORMAL | 1.25 | 27 | 3.25 | 34.35 | 34.35 | Charging | DG | 25 | 25 | 0 | 1.25 | 0 | 23.75
5 | 2 | Night | NORMAL | 3.35 | 27 | 5.35 | 39.28 | 39.28 | Charging | DG | 25 | 25 | 0 | 3.35 | 0 | 21.65
6 | 2 | Day | OFF | 6.28 | 0 | 10 | 28.43 | 28.43 | Discharging | - | 25 | 16.28 | 8.72 | 6.28 | 10 | 0
7 | 2 | Day | OFF | 12.72 | 0 | 10 | 17.59 | 17.59 | Discharging | - | 25 | 22.72 | 2.28 | 12.72 | 10 | 0
8 | 2 | Day | OFF | 26.88 | 0 | 1.88 | 19.32 | 19.32 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
9 | 2 | Day | OFF | 34.82 | 0 | 9.82 | 28.38 | 28.38 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
10 | 2 | Day | OFF | 30.45 | 0 | 5.45 | 33.4 | 33.4 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
11 | 2 | Day | OFF | 27.44 | 0 | 2.44 | 35.65 | 35.65 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
12 | 2 | Day | OFF | 29.18 | 0 | 4.18 | 39.5 | 39.5 | Charging | Solar | 25 | 25 | 0 | 25 | 0 | 0
13 | 2 | Day | OFF | 12.43 | 0 | 10 | 28.66 | 28.66 | Discharging | - | 25 | 22.43 | 2.57 | 12.43 | 10 | 0
14 | 2 | Day | OFF | 15.36 | 0 | 9.64 | 18.2 | 18.2 | Discharging | - | 25 | 25 | 0 | 15.36 | 9.64 | 0
15 | 2 | Day | OFF | 19.44 | 0 | 5.56 | 12.17 | 12.17 | Discharging | - | 25 | 25 | 0 | 19.44 | 5.56 | 0
16 | 2 | Day | OFF | 11.92 | 0 | 2 | 10 | 10 | Discharging | - | 25 | 13.92 | 11.08 | 11.92 | 2 | 0
17 | 2 | Day | OFF | 10.96 | 0 | 0 | 10 | 10 | Idle | - | 25 | 10.96 | 14.04 | 10.96 | 0 | 0
18 | 2 | Night | NORMAL | 4.89 | 27 | 6.89 | 16.35 | 16.35 | Charging | DG | 25 | 25 | 0 | 4.89 | 0 | 20.11
19 | 2 | Night | NORMAL | 1.18 | 27 | 3.18 | 19.28 | 19.28 | Charging | DG | 25 | 25 | 0 | 1.18 | 0 | 23.82
20 | 2 | Night | NORMAL | 0 | 27 | 2 | 21.13 | 21.13 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
21 | 2 | Night | NORMAL | 0 | 27 | 2 | 22.97 | 22.97 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
22 | 2 | Night | NORMAL | 0 | 27 | 2 | 24.82 | 24.82 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25
23 | 2 | Night | NORMAL | 0 | 27 | 2 | 26.66 | 26.66 | Charging | DG | 25 | 25 | 0 | 0 | 0 | 25

## Summary
Template | Total_Deficit_MWh | DG_Hours | Total_DG_MWh
T0: Solar+BESS | 707.96 | 0 | 0
T1: Green Priority | 0 | 37 | 638.9
T2: DG Night Charge | 138.38 | 22 | 533.58
T3: DG Blackout | 354.23 | 22 | 294.8
T4: DG Emergency | 115.91 | 27 | 521.53
T5: DG Day Charge | 517.27 | 16 | 93.35
T6: DG Night SoC | 138.38 | 22 | 533.58